Internship Report – Mytrah Energy Pvt. Ltd.

Name: Adithya Kumar
Roll Number: 111501017
Internship Date: June 5’th 2017 - July 27’th 2017

Objectives:
1. Detection of Performance deviation in WindSpeed vs ActivePower graph
2. Detection of Double trends in RotorSpeed vs ActivePower graph
3. Detection of Double Trends in PitchAngle vs ActivePower graph

Ref:

WindSpeed vs ActivePower

Proper curve:

Curve with Curtailments:

Curve with Double Trends:

RotorSpeed vs ActivePower

Proper curve:

Curve with Double Trends:

PitchAngle vs ActivePower

Proper curve:

Curve with Double Trends:

Noise Filtering

Before trying to act on any curve, we always filter noise in the curve using the DBSCAN algorithm.

WindSpeed vs ActivePower

Methods used or finding the performance degraded points (Double Trends and Curtailments) in order.

Method 1:

Use a clustring algorithm, DBSCAN.

Does it work?:

No, Considering that the data from the wind turbine is defined by the nature, the data is unpredictable.
There will always be a case for which the input eps and min_samples give improper results.
In reality, from the data taken, about 30% of the wind turbines gave improper results, using this method

Ref Images:

Conclusion:

Not Recommended, but can work if we have another kind of algorithm which works on each cluster and marks the cluster accordingly depending on its position on the graph.

Method 2:

Scale the data from 0-1.
Cluster the data using DBSCAN.
Take the maxium cluster and try to fit a Sigmoid curve on the Cluster, shift the sigmoid curve omitting the (probably) correct performance.
Get the points to the right of the sigmoid curve, keeping in mind some edge cases.

Does it work?

If the graph only has curtailments, then mostly yes, it gives satisfying results.

If the graph has double trends, We cannot predict which trend group will have the maxium sized cluster and hence the result is unpredictable.

Also, there could be a case, where the maxium sized cluster is not the tail of the performance curve, if so this method gives wrong results.

I quote “mostly satisfying results” as the power curve does not fit the sigmoid properly. If an assymetrical Sigmoid curve id used, then, there is a high probability for the algorithm of fitting the curve to fail.

Conclusion:

Not Recommended, The results are unpredictable.

Ref Images:

Method 3:

Find the boundary points of the performance curve.

Does it work?

Yes. If the bottom 20% of the data is proper the boundaries will be found and adjusted accordingly based on statistics.

Conclusion:

Semi Recommended, The results are predictable but this method is overkill. There are better ways to get similar results.

Ref Images:

Method 4:

“Most complex problems, have the easiest of the solutions” --Unknown

A very simple and efficient solution, understanding the creks of the problem.

Instead of treating curtailments and double trends seperately, we try to understand, what they really are, In the end both curtailments and double trends can be understood as Abnormal Performance

Our problem of finding curtailments and double treands is now converted into finding the abnormal performance points.
To classify weather the data has abnormality, a perdormanceDropScore is assigned to the data file.

Depending on the performanceDropScore of multiple turbines (similar conditions) the data can be classified accordingly.

Our solution is pretty simple, first remove the duplicate points then discretize the WindSpeed axis and apply DBSCAN on each discritized x-point to cluster the abnormal performance out (with some edge cases).

Conclusion:

Recommended, The results are more predictable. The only effort required is initialisation, ie. finding the proper parameters for the specific.

Ref Images:

PitchAngle vs ActivePower

Methods used for finding the double trends in the the PitchAngle vs ActivePower curve.

The method a human used to identify double trends is by noticing a distinct shift of the curve. We will try to mimic this method in the algorithm.

We give a score to each curve, The score depends on the value of the shifted distance, and how often the shift is.

We first discritize the ActivePower axis, and for each discritized value we try to find the shifted value (with some edge cases). Summing all the shifts gives a score to our data. Depending on the score the data can be classified accordingly.

Ref Images:

RotorSpeed vs ActivePower

Methods used for finding the double trends in the the RotorSpeed vs ActivePower curve. (DFIG Machines only)

We will use a more statistical approach for the solution and hence, we dont remove the duplicate points. Here, the density matters.

We will be utilising a statistical measurement called kurtosis.